## AMPAS (Fig 4-7)
Plate number | AMPAS Device | AMPAS Design | Deposited microorganisms (cfu/55mm plate) | AMPAS Device | Deposited microorganisms (cfu/55mm plate)
1 | A | D (No plastic wrap & 5 mm gap) | 35 | A | 35
1 | A | D (No plastic wrap & 5 mm gap) | 14 | A | 24
1 | A | D (No plastic wrap & 5 mm gap) | 9 | A | 19
2 | A | D (No plastic wrap & 5 mm gap) | 14 | A | 14
2 | A | D (No plastic wrap & 5 mm gap) | 9 | A | 9
2 | A | D (No plastic wrap & 5 mm gap) | 8 | A | 18
3 | A | D (No plastic wrap & 5 mm gap) | 20 | A | 20
3 | A | D (No plastic wrap & 5 mm gap) | 12 | A | 12
3 | A | D (No plastic wrap & 5 mm gap) | 5 | A | 5
4 | A | D (No plastic wrap & 5 mm gap) | 23 | A | 13
4 | A | D (No plastic wrap & 5 mm gap) | 4 | A | 4
4 | A | D (No plastic wrap & 5 mm gap) | 6 | A | 6
5 | A | D (No plastic wrap & 5 mm gap) | 27 | A | 7
5 | A | D (No plastic wrap & 5 mm gap) | 10 | A | 10
5 | A | D (No plastic wrap & 5 mm gap) | 8 | A | 8
6 | A | D (No plastic wrap & 5 mm gap) | 22 | A | 22
6 | A | D (No plastic wrap & 5 mm gap) | 7 | A | 7
6 | A | D (No plastic wrap & 5 mm gap) | 10 | A | 10
1 | B | B (Plastic wrap & 5mm gap) | 34 | B | 34
1 | B | B (Plastic wrap & 5mm gap) | 12 | B | 22
1 | B | B (Plastic wrap & 5mm gap) | 12 | B | 12
2 | B | B (Plastic wrap & 5mm gap) | 7 | B | 7
2 | B | B (Plastic wrap & 5mm gap) | 12 | B | 12
2 | B | B (Plastic wrap & 5mm gap) | 15 | B | 15
3 | B | B (Plastic wrap & 5mm gap) | 4 | B | 14
3 | B | B (Plastic wrap & 5mm gap) | 6 | B | 6
3 | B | B (Plastic wrap & 5mm gap) | 27 | B | 27
4 | B | B (Plastic wrap & 5mm gap) | 8 | B | 8
4 | B | B (Plastic wrap & 5mm gap) | 20 | B | 20
4 | B | B (Plastic wrap & 5mm gap) | 12 | B | 12
5 | B | B (Plastic wrap & 5mm gap) | 6 | B | 6
5 | B | B (Plastic wrap & 5mm gap) | 27 | B | 16
5 | B | B (Plastic wrap & 5mm gap) | 10 | B | 10
6 | B | B (Plastic wrap & 5mm gap) | 22 | B | 22
6 | B | B (Plastic wrap & 5mm gap) | 7 | B | 7
6 | B | B (Plastic wrap & 5mm gap) | 10 | B | 10
1 | C | A (Plastic wrap & 1mm gap) | 34 | C | 34
1 | C | A (Plastic wrap & 1mm gap) | 15 | C | 15
1 | C | A (Plastic wrap & 1mm gap) | 20 | C | 20
2 | C | A (Plastic wrap & 1mm gap) | 7 | C | 7
2 | C | A (Plastic wrap & 1mm gap) | 12 | C | 12
2 | C | A (Plastic wrap & 1mm gap) | 10 | C | 10
3 | C | A (Plastic wrap & 1mm gap) | 13 | C | 13
3 | C | A (Plastic wrap & 1mm gap) | 6 | C | 6
3 | C | A (Plastic wrap & 1mm gap) | 19 | C | 19
4 | C | A (Plastic wrap & 1mm gap) | 22 | C | 14
4 | C | A (Plastic wrap & 1mm gap) | 18 | C | 18
4 | C | A (Plastic wrap & 1mm gap) | 12 | C | 12
5 | C | A (Plastic wrap & 1mm gap) | 16 | C | 16
5 | C | A (Plastic wrap & 1mm gap) | 23 | C | 13
5 | C | A (Plastic wrap & 1mm gap) | 10 | C | 10
6 | C | A (Plastic wrap & 1mm gap) | 22 | C | 12
6 | C | A (Plastic wrap & 1mm gap) | 7 | C | 7
6 | C | A (Plastic wrap & 1mm gap) | 10 | C | 10
1 | D | C (No plastic wrap & 1 mm gap) | 25 | D | 25
1 | D | C (No plastic wrap & 1 mm gap) | 5 | D | 15
1 | D | C (No plastic wrap & 1 mm gap) | 10 | D | 10
2 | D | C (No plastic wrap & 1 mm gap) | 25 | D | 25
2 | D | C (No plastic wrap & 1 mm gap) | 6 | D | 16
2 | D | C (No plastic wrap & 1 mm gap) | 6 | D | 6
3 | D | C (No plastic wrap & 1 mm gap) | 11 | D | 11
3 | D | C (No plastic wrap & 1 mm gap) | 4 | D | 4
3 | D | C (No plastic wrap & 1 mm gap) | 10 | D | 10
4 | D | C (No plastic wrap & 1 mm gap) | 20 | D | 12
4 | D | C (No plastic wrap & 1 mm gap) | 8 | D | 8
4 | D | C (No plastic wrap & 1 mm gap) | 5 | D | 5
5 | D | C (No plastic wrap & 1 mm gap) | 27 | D | 11
5 | D | C (No plastic wrap & 1 mm gap) | 8 | D | 8
5 | D | C (No plastic wrap & 1 mm gap) | 18 | D | 18
6 | D | C (No plastic wrap & 1 mm gap) | 21 | D | 14
6 | D | C (No plastic wrap & 1 mm gap) | 8 | D | 8
6 | D | C (No plastic wrap & 1 mm gap) | 8 | D | 8

## Table 1
ACH | Air sampling collection point | Bioaerosols load |  | Deposited microorganism load
|  | (cfu.m-3) |  | (cfu.m-2.h-1)
|  | Mean ± SD | Reduction percentage | Mean ± SD | Reduction percentage
|  | (Min-Max), n=sample size |  | (Min-Max)
3 | Near supply air | 3797 ± 426 |  | 3696 ± 1885
| (Inlet) | (2878 - 4437), |  | (758 - 7036),
|  | n=15 |  | n=15
| Near extract air | 5599 ± 565 |  | 9450 ± 4469
| (Outlet) | (4376 - 6767), |  | (4363 - 22171),
|  | n=15 |  | n=15
| Mean across both locations | 4698 ± 1035 |  | 6573 ± 4470
|  | (2878 - 6767), |  | (758 - 22171),
|  | n=30 |  | n=30
6 | Near supply air | 2218 ± 350 | 43% ± 8% | 2442 ± 910 | 33% ± 25%
| (Inlet) | (1669 - 2861), |  | (505 - 4042),
|  | n=15 |  | n=15
| Near extract air | 3167 ± 580 | 45% ± 10% | 5086 ± 2961 | 44% ± 32%
| (Outlet) | (1933 - 4571), |  | (1011 - 10611),
|  | n=15 |  | n=15
| Mean across both locations | 2693 ± 674 |  | 3764 ± 2548
|  | (1669 - 4571), |  | (505 - 10611),
|  | n=30 |  | n=30

## Fig 8, 9 & 11
Ventilation rate (ACH) | Sampling point | Bioaerosols load (cfu.m-3) | Deposited microorganism load (cfu.m-2.h-1) | loss rate due to deposition onto floor (h-1)
6 | Near supply air | 2000 | 3031.5789 | 0.66192
6 | Near supply air | 1669 | 1515.7895 | 0.39659
6 | Near supply air | 1964 | 3536.8421 | 0.78639
6 | Near supply air | 1825 | 3031.5789 | 0.72539
6 | Near supply air | 1852 | 3536.8421 | 0.83395
6 | Near supply air | 2491 | 4042.1053 | 0.7086
6 | Near supply air | 2392 | 3031.5789 | 0.55344
6 | Near supply air | 2607 | 3031.5789 | 0.5078
6 | Near supply air | 2593 | 2526.3158 | 0.42545
6 | Near supply air | 2678 | 2021.0526 | 0.32956
6 | Near supply air | 2401.7857 | 2526.3158 | 0.45932
6 | Near supply air | 2218.75 | 2021.0526 | 0.39777
6 | Near supply air | 2861.6071 | 2526.3158 | 0.38552
6 | Near supply air | 2852.6786 | 2526.3158 | 0.38672
6 | Near supply air | 2642.8571 | 1010.5263 | 0.16697
6 | Near supply air | 2151 | 1515.7895 | 0.30773
6 | Near supply air | 2441 | 3031.5789 | 0.54233
6 | Near supply air | 1678 | 2526.3158 | 0.65745
6 | Near supply air | 1941 | 2526.3158 | 0.56836
6 | Near supply air | 1669 | 1010.5263 | 0.2644
6 | Near supply air | 2120 | 1515.7895 | 0.31222
6 | Near supply air | 2049 | 505.2632 | 0.10768
6 | Near supply air | 2308 | 2526.3158 | 0.47799
6 | Near supply air | 1862 | 2526.3158 | 0.59248
6 | Near supply air | 2357 | 2526.3158 | 0.46805
6 | Near supply air | 2352 | 3536.8421 | 0.65666
6 | Near supply air | 2120 | 2526.3158 | 0.52037
6 | Near supply air | 2290 | 3031.5789 | 0.57809
6 | Near supply air | 1745 | 3536.8421 | 0.88508
6 | Near supply air | 2424 | 505.2632 | 0.091023
6 | Near extract air | 3955 | 3031.5789 | 0.33472
6 | Near extract air | 3750 | 4042.1053 | 0.4707
6 | Near extract air | 3616 | 2021.0526 | 0.24407
6 | Near extract air | 3691 | 3031.5789 | 0.35867
6 | Near extract air | 3566 | 3031.5789 | 0.37124
6 | Near extract air | 3125 | 2526.3158 | 0.35302
6 | Near extract air | 2660 | 4042.1053 | 0.66358
6 | Near extract air | 2441 | 2021.0526 | 0.36155
6 | Near extract air | 2477 | 4042.1053 | 0.7126
6 | Near extract air | 2526 | 2021.0526 | 0.34939
6 | Near extract air | 1933 | 1010.5263 | 0.22829
6 | Near extract air | 2339 | 2021.0526 | 0.37732
6 | Near extract air | 2357 | 2526.3158 | 0.46805
6 | Near extract air | 2843 | 4547.3684 | 0.69847
6 | Near extract air | 2991 | 2526.3158 | 0.36884
6 | Near extract air | 3946 | 9094.7368 | 1.0065
6 | Near extract air | 3459 | 10105.2632 | 1.2757
6 | Near extract air | 3598 | 6568.4211 | 0.79719
6 | Near extract air | 3183 | 8589.4737 | 1.1784
6 | Near extract air | 2950 | 10610.5263 | 1.5707
6 | Near extract air | 3669 | 10610.5263 | 1.2629
6 | Near extract air | 3303 | 8589.4737 | 1.1356
6 | Near extract air | 3147 | 9600 | 1.3321
6 | Near extract air | 4571 | 5557.8947 | 0.53096
6 | Near extract air | 3040 | 5557.8947 | 0.79836
6 | Near extract air | 3125 | 5052.6316 | 0.70604
6 | Near extract air | 3620 | 3031.5789 | 0.3657
6 | Near extract air | 3200 | 5052.6316 | 0.6895
6 | Near extract air | 2901 | 4042.1053 | 0.60845
6 | Near extract air | 3022 | 8084.2105 | 1.1682
3 | Near supply air | 3660 | 2301.7544 | 0.27463
3 | Near supply air | 3830 | 4852.7887 | 0.5533
3 | Near supply air | 3607 | 5777.1599 | 0.69941
3 | Near supply air | 4196 | 6100.2414 | 0.63486
3 | Near supply air | 3910 | 6032.1707 | 0.67369
3 | Near supply air | 3580 | 5809.6208 | 0.70865
3 | Near supply air | 3892 | 758.3296 | 0.085084
3 | Near supply air | 4419 | 931.4907 | 0.092049
3 | Near supply air | 3946 | 3196.0832 | 0.35369
3 | Near supply air | 4223 | 2616.6731 | 0.27058
3 | Near supply air | 3321 | 5408.8603 | 0.71122
3 | Near supply air | 3848 | 957.2238 | 0.10863
3 | Near supply air | 3758 | 3038.797 | 0.35311
3 | Near supply air | 4437 | 4322.1306 | 0.42538
3 | Near supply air | 3339 | 2392.0053 | 0.31283
3 | Near supply air | 4160 | 2386.3442 | 0.2505
3 | Near supply air | 3321 | 2237.594 | 0.29422
3 | Near supply air | 3357 | 7036.2573 | 0.91528
3 | Near supply air | 2983 | 3545.5947 | 0.51904
3 | Near supply air | 2878 | 936.1887 | 0.14205
3 | Near supply air | 3830 | 1563.1579 | 0.17822
3 | Near supply air | 4200 | 4418.4811 | 0.4594
3 | Near supply air | 4366 | 3977.0412 | 0.39778
3 | Near supply air | 3705 | 4402.8181 | 0.51893
3 | Near supply air | 3401 | 3645.933 | 0.46813
3 | Near supply air | 4419 | 1689.9004 | 0.16699
3 | Near supply air | 3946 | 2779.9956 | 0.30765
3 | Near supply air | 4223 | 5242.9135 | 0.54215
3 | Near supply air | 3321 | 6729.9502 | 0.88493
3 | Near supply air | 3848 | 5785.1193 | 0.65651
3 | Near extract air | 5410 | 16503.8298 | 1.3321
3 | Near extract air | 5580 | 6784.5395 | 0.53095
3 | Near extract air | 5357 | 9793.6471 | 0.79834
3 | Near extract air | 5946 | 9614.4361 | 0.7061
3 | Near extract air | 5660 | 4739.8793 | 0.36569
3 | Near extract air | 5330 | 8414.0057 | 0.68935
3 | Near extract air | 5642 | 14344.2569 | 1.1102
3 | Near extract air | 6169 | 5330.3335 | 0.37732
3 | Near extract air | 5696 | 6105.2632 | 0.46806
3 | Near extract air | 5973 | 9551.6153 | 0.69831
3 | Near extract air | 5767 | 4871.6418 | 0.36888
3 | Near extract air | 5267 | 8002.8259 | 0.66351
3 | Near extract air | 5991 | 4958.4143 | 0.36142
3 | Near extract air | 6357 | 10370.8622 | 0.71241
3 | Near extract air | 5455 | 4363.4741 | 0.3493
3 | Near extract air | 4910 | 10803.1 | 0.9608
3 | Near extract air | 5148 | 9136.1757 | 0.77498
3 | Near extract air | 5203 | 19875.8952 | 1.6682
3 | Near extract air | 5245 | 5138.0149 | 0.42777
3 | Near extract air | 4376 | 11763.1195 | 1.1738
3 | Near extract air | 5937 | 13062.0871 | 0.96075
3 | Near extract air | 6511 | 11555.2043 | 0.77499
3 | Near extract air | 6767 | 22170.8204 | 1.4307
3 | Near extract air | 5743 | 12634.0487 | 0.96066
3 | Near extract air | 5272 | 5363.8769 | 0.44429
3 | Near extract air | 5203 | 6326.2737 | 0.53096
3 | Near extract air | 5245 | 9589.1558 | 0.79836
3 | Near extract air | 4376 | 7076.4559 | 0.70616
3 | Near extract air | 5937 | 4971.6998 | 0.36568
3 | Near extract air | 6511 | 10278.3244 | 0.68935